## WithoutAirBarrier
Infiltration inputs for five buildings in eight climate zones for buildings without an air barrier
| Highrise Apartment | Hospital | Large Hotel | Medium Office | Midrise Apartment | Primary School | Secondary School | Small Hotel | Small Office | Stand Alone Retail | Strip Mall
Design leakage rate @ 75 Pa (m3/h/m2) - 5 sided | 13.8
Idesign @ 4 Pa (m3/s/m2) - 5 sided | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00056896 | 0.00057033
| Highrise Apartment | Hospital | Large Hotel | Medium Office | Midrise Apartment | Primary School | Secondary School | Small Hotel | Small Office | Stand Alone Retail | Strip Mall
Miami (CZ 1)
A on | 0.073583 | 0.073823 | 0.25795 | -0.019776 | 0.056732 | 0.0071519 | 0.097299 | 0.044993 | 0.04954 | -0.022595 | 0.030616
B on | 0.011715 | -1.1493e-05 | 0.019414 | -0.0015664 | 0.0050477 | -0.00076427 | 0.00050097 | 0.004083 | -0.0017688 | -0.004433 | -0.0020934
D on | 0.024809 | 0.0084096 | 0.027226 | 0.028725 | 0.037266 | 0.030975 | 0.083922 | 0.0078663 | 0.11401 | 0.042866 | 0.034034
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.012451 | #N/A | 0.004095 | 0.012189 | #N/A | 0.018827 | 0.0086578 | 0.012743
D off | #N/A | #N/A | #N/A | 0.038028 | #N/A | 0.042736 | 0.10889 | #N/A | 0.1349 | 0.057732 | 0.044764
Phoenix (CZ 2)
A on | 0.07738 | 0.076549 | 0.27081 | -0.010263 | 0.054276 | 0.0018586 | 0.065728 | 0.041026 | 0.03023 | -0.0047537 | 0.022752
B on | 0.013442 | 0.00027303 | 0.014575 | -0.00069306 | 0.0052334 | -0.00056666 | -0.0023098 | 0.0067385 | -0.0023485 | -0.0014044 | -0.0016212
D on | 0.016704 | 0.0065408 | 0.02309 | 0.023056 | 0.028191 | 0.029816 | 0.085304 | 0.0052648 | 0.11045 | 0.030713 | 0.029919
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.016389 | #N/A | 0.0051901 | 0.012232 | #N/A | 0.018826 | 0.0096851 | 0.01003
D off | #N/A | #N/A | #N/A | 0.030751 | #N/A | 0.034823 | 0.096493 | #N/A | 0.12089 | 0.052372 | 0.044994
Memphis (CZ 3)
A on | 0.091355 | 0.061036 | 0.33031 | -0.045091 | 0.06474 | -0.0038875 | 0.064701 | 0.026863 | 0.0209 | -0.062893 | 0.0036785
B on | 0.014458 | 0.002056 | 0.0039023 | 0.0046488 | 0.0064575 | 0.0030673 | 0.0077748 | 0.0082968 | 0.0064318 | 0.0072249 | 0.0049897
D on | 0.026463 | 0.0097806 | 0.032991 | 0.032714 | 0.041544 | 0.039313 | 0.10549 | 0.009573 | 0.1297 | 0.044744 | 0.046039
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.017296 | #N/A | 0.007001 | 0.016846 | #N/A | 0.017911 | 0.011087 | 0.0097354
D off | #N/A | #N/A | #N/A | 0.039839 | #N/A | 0.051549 | 0.13139 | #N/A | 0.14727 | 0.059317 | 0.059559
Baltimore (CZ 4)
A on | 0.10581 | 0.056831 | 0.33491 | -0.046095 | 0.071569 | -0.0027508 | 0.072476 | 0.028654 | 0.023753 | -0.058131 | 0.0051137
B on | 0.014454 | 0.0022744 | 0.0041409 | 0.005309 | 0.0068392 | 0.0036988 | 0.0090916 | 0.0085742 | 0.0078055 | 0.0072576 | 0.005938
D on | 0.021441 | 0.010137 | 0.026609 | 0.031121 | 0.034181 | 0.033634 | 0.08926 | 0.0085898 | 0.11586 | 0.043559 | 0.036782
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.017404 | #N/A | 0.0073347 | 0.017442 | #N/A | 0.01817 | 0.011233 | 0.0099781
D off | #N/A | #N/A | #N/A | 0.034101 | #N/A | 0.0397 | 0.10163 | #N/A | 0.1187 | 0.052274 | 0.044135
Chicago (CZ 5)
A on | 0.13019 | 0.047652 | 0.33298 | -0.044486 | 0.091718 | 0.0024599 | 0.10191 | 0.040302 | 0.043092 | -0.044075 | 0.01644
B on | 0.012865 | 0.0027822 | 0.0049201 | 0.0055419 | 0.0058874 | 0.0034379 | 0.0077275 | 0.007883 | 0.007448 | 0.0066422 | 0.0054082
D on | 0.020562 | 0.010732 | 0.026198 | 0.02953 | 0.032767 | 0.034034 | 0.087666 | 0.0077757 | 0.10956 | 0.037599 | 0.035997
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.015477 | #N/A | 0.0065615 | 0.015581 | #N/A | 0.01636 | 0.010005 | 0.0090268
D off | #N/A | #N/A | #N/A | 0.034434 | #N/A | 0.042256 | 0.10501 | #N/A | 0.11729 | 0.049293 | 0.047119
Helena (CZ 6)
A on | 0.10747 | 0.057119 | 0.33572 | -0.038213 | 0.069666 | -0.0042899 | 0.079819 | 0.028254 | 0.020797 | -0.045314 | 0.0016928
B on | 0.011991 | 0.0019534 | 0.0036749 | 0.0042297 | 0.005876 | 0.0030229 | 0.0061196 | 0.0070806 | 0.0068475 | 0.0053644 | 0.0048064
D on | 0.013479 | 0.0070695 | 0.017311 | 0.020609 | 0.021609 | 0.021498 | 0.058957 | 0.0062234 | 0.076386 | 0.031663 | 0.022476
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.013928 | #N/A | 0.005593 | 0.01245 | #N/A | 0.015431 | 0.0086109 | 0.0081319
D off | #N/A | #N/A | #N/A | 0.026354 | #N/A | 0.030546 | 0.077908 | #N/A | 0.078379 | 0.040649 | 0.028007
Duluth (CZ 7)
A on | 0.14014 | 0.035912 | 0.32646 | -0.050594 | 0.089232 | 0.0034698 | 0.10158 | 0.040351 | 0.048833 | -0.045003 | 0.007034
B on | 0.012127 | 0.0033089 | 0.0059082 | 0.005873 | 0.0060209 | 0.0035631 | 0.0083885 | 0.0076456 | 0.0075635 | 0.0062664 | 0.0057216
D on | 0.016742 | 0.010497 | 0.020482 | 0.026271 | 0.027437 | 0.027222 | 0.072969 | 0.0068643 | 0.092015 | 0.03738 | 0.02924
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.014217 | #N/A | 0.0060633 | 0.014407 | #N/A | 0.015208 | 0.0093164 | 0.0087038
D off | #N/A | #N/A | #N/A | 0.029846 | #N/A | 0.036069 | 0.090884 | #N/A | 0.094703 | 0.04564 | 0.036165
Fairbanks (CZ 8)
A on | 0.1235 | 0.033424 | 0.29056 | -0.076022 | 0.064115 | -0.015343 | 0.031585 | 0.02665 | -0.029808 | -0.059189 | -0.018662
B on | 0.013359 | 0.0043516 | 0.0083895 | 0.0076648 | 0.0071346 | 0.0039899 | 0.0087366 | 0.0084844 | 0.010959 | 0.0068637 | 0.0063118
D on | 0.021661 | 0.0089766 | 0.029648 | 0.031044 | 0.036359 | 0.039176 | 0.1116 | 0.0090281 | 0.13108 | 0.046638 | 0.04458
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.014289 | #N/A | 0.0056824 | 0.012542 | #N/A | 0.016608 | 0.0087033 | 0.0082682
D off | #N/A | #N/A | #N/A | 0.03586 | #N/A | 0.050257 | 0.12725 | #N/A | 0.10461 | 0.067678 | 0.059119

## WithAirBarrier
Infiltration inputs for five buildings in eight climate zones for buildings with an air barrier
| Highrise Apartment | Hospital | Large Hotel Hotel | Medium Office | Midrise Apartment | Primary School | Secondary School | Small Hotel | Small Office | Stand Alone Retail | Strip Mall
Design leakage rate @ 75 Pa (m3/h/m2) - 5 sided | 5
Volume (m3) | 23884.04 | 79802 | 30358.65 | 19741.41 | 9553.8 | 27484 | 95216 | 11621.72 | 1559.02 | 13984.18 | 10827.84
Exterior surface area - 5-sided (m2) | 4638.66 | 8936.73 | 6004.69 | 3638.45 | 2325.7 | 9383 | 18286 | 2698.13 | 282 | 3471 | 3274.4
Exterior surface area - 6-sided (m2) | 5422.32 | 13107.26 | 8429.4546 | 5299.18 | 3109.36 | 16254 | 30188 | 3701.53 | 643 | 5764.99 | 5364.7
Idesign @ 4 Pa (m3/s/m2) - 5 sided | 0.00024219 | 0.00030388 | 0.00029086 | 0.00030176 | 0.00027701 | 0.00035891 | 0.00034205 | 0.00028424 | 0.00046801 | 0.00034412 | 0.00033946
| Highrise Apartment | Hospital | Large Hotel Hotel | Medium Office | Midrise Apartment | Primary School | Secondary School | Small Hotel | Small Office | Stand Alone Retail | Strip Mall
Miami (CZ 1)
A on | 0.10092 | 0.14356 | 0.47471 | -0.024874 | 0.06599 | -0.0028214 | 0.1024 | 0.052705 | 0.046434 | -0.081524 | 0.039469
B on | 0.02315 | -0.00013311 | 0.032096 | -0.0014025 | 0.0072986 | -0.00073239 | 0.00023945 | 0.0034995 | -0.0018424 | -0.0037807 | -0.0026267
D on | 0.024259 | 0.0050186 | 0.034197 | 0.016071 | 0.040246 | 0.027825 | 0.086968 | 0.0067916 | 0.11258 | 0.04553 | 0.0338
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.012901 | #N/A | 0.0040635 | 0.012486 | #N/A | 0.01927 | 0.012536 | 0.015433
D off | #N/A | #N/A | #N/A | 0.038318 | #N/A | 0.042585 | 0.11307 | #N/A | 0.13321 | 0.081666 | 0.047342
Phoenix (CZ 2)
A on | 0.1237 | 0.14669 | 0.49962 | -0.0092047 | 0.070883 | -0.003145 | 0.068862 | 0.046676 | 0.029124 | -0.055038 | 0.041293
B on | 0.026401 | -0.00012932 | 0.023313 | -0.00054343 | 0.0088226 | -0.00048868 | -0.0025184 | 0.0056804 | -0.0023813 | -0.0016532 | -0.0027276
D on | 0.011922 | 0.0031695 | 0.030274 | 0.011559 | 0.026537 | 0.025243 | 0.088765 | 0.0048768 | 0.10826 | 0.036399 | 0.02795
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.016907 | #N/A | 0.0051613 | 0.012829 | #N/A | 0.019532 | 0.013876 | 0.011761
D off | #N/A | #N/A | #N/A | 0.031441 | #N/A | 0.034707 | 0.099766 | #N/A | 0.11869 | 0.074217 | 0.050781
Memphis (CZ 3)
A on | 0.12822 | 0.14024 | 0.60506 | -0.040296 | 0.074819 | -0.014001 | 0.065908 | 0.031194 | 0.016941 | -0.14105 | 0.0042823
B on | 0.029998 | 0.00062739 | 0.0048521 | 0.0016391 | 0.01169 | 0.0021945 | 0.0086722 | 0.006518 | 0.0067141 | 0.0089081 | 0.00589
D on | 0.026898 | 0.0047621 | 0.03845 | 0.019011 | 0.043576 | 0.037162 | 0.11064 | 0.0089499 | 0.12801 | 0.052708 | 0.047739
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.017628 | #N/A | 0.006966 | 0.017833 | #N/A | 0.018559 | 0.015728 | 0.011215
D off | #N/A | #N/A | #N/A | 0.040227 | #N/A | 0.051381 | 0.13735 | #N/A | 0.14456 | 0.084177 | 0.066054
Baltimore (CZ 4)
A on | 0.15654 | 0.14193 | 0.60807 | -0.045345 | 0.086478 | -0.014625 | 0.073188 | 0.029606 | 0.019619 | -0.14115 | 0.0028853
B on | 0.029226 | 0.00054771 | 0.0053411 | 0.0017748 | 0.011965 | 0.0027358 | 0.010161 | 0.0068726 | 0.0081361 | 0.0086049 | 0.006934
D on | 0.022081 | 0.0040655 | 0.031519 | 0.019682 | 0.035587 | 0.032595 | 0.093551 | 0.0081702 | 0.11408 | 0.052674 | 0.038718
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.017674 | #N/A | 0.0073028 | 0.018479 | #N/A | 0.018817 | 0.015917 | 0.011431
D off | #N/A | #N/A | #N/A | 0.034237 | #N/A | 0.039575 | 0.10625 | #N/A | 0.11596 | 0.074226 | 0.048617
Chicago (CZ 5)
A on | 0.19152 | 0.13975 | 0.59262 | -0.063403 | 0.11161 | -0.013364 | 0.10456 | 0.033591 | 0.039077 | -0.13601 | 0.012848
B on | 0.026444 | 0.00066422 | 0.0075516 | 0.002367 | 0.010574 | 0.0026972 | 0.0086771 | 0.0066767 | 0.007786 | 0.0082176 | 0.006467
D on | 0.020718 | 0.0045216 | 0.030408 | 0.021915 | 0.033958 | 0.033315 | 0.091988 | 0.0075994 | 0.10779 | 0.048129 | 0.038236
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.015646 | #N/A | 0.0065341 | 0.016491 | #N/A | 0.016967 | 0.014172 | 0.010334
D off | #N/A | #N/A | #N/A | 0.034663 | #N/A | 0.042119 | 0.11004 | #N/A | 0.11449 | 0.069976 | 0.052341
Helena (CZ 6)
A on | 0.1689 | 0.14191 | 0.61053 | -0.032803 | 0.087671 | -0.013412 | 0.082164 | 0.027076 | 0.016183 | -0.12215 | -0.0017935
B on | 0.023158 | 0.00056708 | 0.0046377 | 0.0011403 | 0.0097381 | 0.0021701 | 0.0068405 | 0.0056615 | 0.0071768 | 0.0064278 | 0.0055184
D on | 0.014267 | 0.0023928 | 0.02155 | 0.014474 | 0.023303 | 0.020052 | 0.061696 | 0.0059885 | 0.07517 | 0.037316 | 0.023779
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.014143 | #N/A | 0.0055693 | 0.013164 | #N/A | 0.016087 | 0.012213 | 0.0092673
D off | #N/A | #N/A | #N/A | 0.026525 | #N/A | 0.030458 | 0.081636 | #N/A | 0.075481 | 0.057649 | 0.031192
Duluth (CZ 7)
A on | 0.22296 | 0.13677 | 0.57598 | -0.067527 | 0.1141 | -0.01438 | 0.10561 | 0.027262 | 0.044565 | -0.14129 | 0.0001995
B on | 0.024004 | 0.00080465 | 0.009495 | 0.0024988 | 0.010318 | 0.0029537 | 0.0092622 | 0.0067599 | 0.0079227 | 0.0079261 | 0.0068505
D on | 0.017173 | 0.004453 | 0.023619 | 0.020783 | 0.028243 | 0.026733 | 0.076459 | 0.0068236 | 0.09018 | 0.047455 | 0.031356
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.014347 | #N/A | 0.0060382 | 0.015229 | #N/A | 0.015784 | 0.013199 | 0.009967
D off | #N/A | #N/A | #N/A | 0.030073 | #N/A | 0.035953 | 0.09552 | #N/A | 0.09127 | 0.064803 | 0.040234
Fairbanks (CZ 8)
A on | 0.22016 | 0.13642 | 0.51854 | -0.056857 | 0.09384 | -0.031734 | 0.03254 | 0.012833 | -0.035764 | -0.15692 | -0.026236
B on | 0.024673 | 0.0011959 | 0.014087 | 0.003261 | 0.011065 | 0.0035193 | 0.0095056 | 0.0076459 | 0.011454 | 0.0087737 | 0.0072638
D on | 0.023371 | 0.0040444 | 0.034196 | 0.016715 | 0.038787 | 0.036547 | 0.11767 | 0.0087861 | 0.12951 | 0.056708 | 0.048615
A off | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | 0 | 0 | 0
B off | #N/A | #N/A | #N/A | 0.014423 | #N/A | 0.0056584 | 0.013243 | #N/A | 0.017368 | 0.012339 | 0.009433
D off | #N/A | #N/A | #N/A | 0.035897 | #N/A | 0.050122 | 0.13379 | #N/A | 0.10014 | 0.09598 | 0.066704

## MeasureFormat
building_type | climate_zone | air_barrier | hvac_status | a | b | d
HighriseApartment | 1 | no | on | 0.073583 | 0.011715 | 0.024809
HighriseApartment | 1 | no | off
HighriseApartment | 2 | no | on | 0.07738 | 0.013442 | 0.016704
HighriseApartment | 2 | no | off
HighriseApartment | 3 | no | on | 0.091355 | 0.014458 | 0.026463
HighriseApartment | 3 | no | off
HighriseApartment | 4 | no | on | 0.10581 | 0.014454 | 0.021441
HighriseApartment | 4 | no | off
HighriseApartment | 5 | no | on | 0.13019 | 0.012865 | 0.020562
HighriseApartment | 5 | no | off
HighriseApartment | 6 | no | on | 0.10747 | 0.011991 | 0.013479
HighriseApartment | 6 | no | off
HighriseApartment | 7 | no | on | 0.14014 | 0.012127 | 0.016742
HighriseApartment | 7 | no | off
HighriseApartment | 8 | no | on | 0.1235 | 0.013359 | 0.021661
HighriseApartment | 8 | no | off
Hospital | 1 | no | on | 0.073823 | -1.1493e-05 | 0.0084096
Hospital | 1 | no | off
Hospital | 2 | no | on | 0.076549 | 0.00027303 | 0.0065408
Hospital | 2 | no | off
Hospital | 3 | no | on | 0.061036 | 0.002056 | 0.0097806
Hospital | 3 | no | off
Hospital | 4 | no | on | 0.056831 | 0.0022744 | 0.010137
Hospital | 4 | no | off
Hospital | 5 | no | on | 0.047652 | 0.0027822 | 0.010732
Hospital | 5 | no | off
Hospital | 6 | no | on | 0.057119 | 0.0019534 | 0.0070695
Hospital | 6 | no | off
Hospital | 7 | no | on | 0.035912 | 0.0033089 | 0.010497
Hospital | 7 | no | off
Hospital | 8 | no | on | 0.033424 | 0.0043516 | 0.0089766
Hospital | 8 | no | off
LargeHotel | 1 | no | on | 0.25795 | 0.019414 | 0.027226
LargeHotel | 1 | no | off
LargeHotel | 2 | no | on | 0.27081 | 0.014575 | 0.02309
LargeHotel | 2 | no | off
LargeHotel | 3 | no | on | 0.33031 | 0.0039023 | 0.032991
LargeHotel | 3 | no | off
LargeHotel | 4 | no | on | 0.33491 | 0.0041409 | 0.026609
LargeHotel | 4 | no | off
LargeHotel | 5 | no | on | 0.33298 | 0.0049201 | 0.026198
LargeHotel | 5 | no | off
LargeHotel | 6 | no | on | 0.33572 | 0.0036749 | 0.017311
LargeHotel | 6 | no | off
LargeHotel | 7 | no | on | 0.32646 | 0.0059082 | 0.020482
LargeHotel | 7 | no | off
LargeHotel | 8 | no | on | 0.29056 | 0.0083895 | 0.029648
LargeHotel | 8 | no | off
MediumOffice | 1 | no | on | -0.019776 | -0.0015664 | 0.028725
MediumOffice | 1 | no | off | 0 | 0.012451 | 0.038028
MediumOffice | 2 | no | on | -0.010263 | -0.00069306 | 0.023056
MediumOffice | 2 | no | off | 0 | 0.016389 | 0.030751
MediumOffice | 3 | no | on | -0.045091 | 0.0046488 | 0.032714
MediumOffice | 3 | no | off | 0 | 0.017296 | 0.039839
MediumOffice | 4 | no | on | -0.046095 | 0.005309 | 0.031121
MediumOffice | 4 | no | off | 0 | 0.017404 | 0.034101
MediumOffice | 5 | no | on | -0.044486 | 0.0055419 | 0.02953
MediumOffice | 5 | no | off | 0 | 0.015477 | 0.034434
MediumOffice | 6 | no | on | -0.038213 | 0.0042297 | 0.020609
MediumOffice | 6 | no | off | 0 | 0.013928 | 0.026354
MediumOffice | 7 | no | on | -0.050594 | 0.005873 | 0.026271
MediumOffice | 7 | no | off | 0 | 0.014217 | 0.029846
MediumOffice | 8 | no | on | -0.076022 | 0.0076648 | 0.031044
MediumOffice | 8 | no | off | 0 | 0.014289 | 0.03586
MidriseApartment | 1 | no | on | 0.056732 | 0.0050477 | 0.037266
MidriseApartment | 1 | no | off
MidriseApartment | 2 | no | on | 0.054276 | 0.0052334 | 0.028191
MidriseApartment | 2 | no | off
MidriseApartment | 3 | no | on | 0.06474 | 0.0064575 | 0.041544
MidriseApartment | 3 | no | off
MidriseApartment | 4 | no | on | 0.071569 | 0.0068392 | 0.034181
MidriseApartment | 4 | no | off
MidriseApartment | 5 | no | on | 0.091718 | 0.0058874 | 0.032767
MidriseApartment | 5 | no | off
MidriseApartment | 6 | no | on | 0.069666 | 0.005876 | 0.021609
MidriseApartment | 6 | no | off
MidriseApartment | 7 | no | on | 0.089232 | 0.0060209 | 0.027437
MidriseApartment | 7 | no | off
MidriseApartment | 8 | no | on | 0.064115 | 0.0071346 | 0.036359
MidriseApartment | 8 | no | off
PrimarySchool | 1 | no | on | 0.0071519 | -0.00076427 | 0.030975
PrimarySchool | 1 | no | off | 0 | 0.004095 | 0.042736
PrimarySchool | 2 | no | on | 0.0018586 | -0.00056666 | 0.029816
PrimarySchool | 2 | no | off | 0 | 0.0051901 | 0.034823
PrimarySchool | 3 | no | on | -0.0038875 | 0.0030673 | 0.039313
PrimarySchool | 3 | no | off | 0 | 0.007001 | 0.051549
PrimarySchool | 4 | no | on | -0.0027508 | 0.0036988 | 0.033634
PrimarySchool | 4 | no | off | 0 | 0.0073347 | 0.0397
PrimarySchool | 5 | no | on | 0.0024599 | 0.0034379 | 0.034034
PrimarySchool | 5 | no | off | 0 | 0.0065615 | 0.042256
PrimarySchool | 6 | no | on | -0.0042899 | 0.0030229 | 0.021498
PrimarySchool | 6 | no | off | 0 | 0.005593 | 0.030546
PrimarySchool | 7 | no | on | 0.0034698 | 0.0035631 | 0.027222
PrimarySchool | 7 | no | off | 0 | 0.0060633 | 0.036069
PrimarySchool | 8 | no | on | -0.015343 | 0.0039899 | 0.039176
PrimarySchool | 8 | no | off | 0 | 0.0056824 | 0.050257
SecondarySchool | 1 | no | on | 0.097299 | 0.00050097 | 0.083922
SecondarySchool | 1 | no | off | 0 | 0.012189 | 0.10889
SecondarySchool | 2 | no | on | 0.065728 | -0.0023098 | 0.085304
SecondarySchool | 2 | no | off | 0 | 0.012232 | 0.096493
SecondarySchool | 3 | no | on | 0.064701 | 0.0077748 | 0.10549
SecondarySchool | 3 | no | off | 0 | 0.016846 | 0.13139
SecondarySchool | 4 | no | on | 0.072476 | 0.0090916 | 0.08926
SecondarySchool | 4 | no | off | 0 | 0.017442 | 0.10163
SecondarySchool | 5 | no | on | 0.10191 | 0.0077275 | 0.087666
SecondarySchool | 5 | no | off | 0 | 0.015581 | 0.10501
SecondarySchool | 6 | no | on | 0.079819 | 0.0061196 | 0.058957
SecondarySchool | 6 | no | off | 0 | 0.01245 | 0.077908
SecondarySchool | 7 | no | on | 0.10158 | 0.0083885 | 0.072969
SecondarySchool | 7 | no | off | 0 | 0.014407 | 0.090884
SecondarySchool | 8 | no | on | 0.031585 | 0.0087366 | 0.1116
SecondarySchool | 8 | no | off | 0 | 0.012542 | 0.12725
SmallHotel | 1 | no | on | 0.044993 | 0.004083 | 0.0078663
SmallHotel | 1 | no | off
SmallHotel | 2 | no | on | 0.041026 | 0.0067385 | 0.0052648
SmallHotel | 2 | no | off
SmallHotel | 3 | no | on | 0.026863 | 0.0082968 | 0.009573
SmallHotel | 3 | no | off
SmallHotel | 4 | no | on | 0.028654 | 0.0085742 | 0.0085898
SmallHotel | 4 | no | off
SmallHotel | 5 | no | on | 0.040302 | 0.007883 | 0.0077757
SmallHotel | 5 | no | off
SmallHotel | 6 | no | on | 0.028254 | 0.0070806 | 0.0062234
SmallHotel | 6 | no | off
SmallHotel | 7 | no | on | 0.040351 | 0.0076456 | 0.0068643
SmallHotel | 7 | no | off
SmallHotel | 8 | no | on | 0.02665 | 0.0084844 | 0.0090281
SmallHotel | 8 | no | off
SmallOffice | 1 | no | on | 0.04954 | -0.0017688 | 0.11401
SmallOffice | 1 | no | off | 0 | 0.018827 | 0.1349
SmallOffice | 2 | no | on | 0.03023 | -0.0023485 | 0.11045
SmallOffice | 2 | no | off | 0 | 0.018826 | 0.12089
SmallOffice | 3 | no | on | 0.0209 | 0.0064318 | 0.1297
SmallOffice | 3 | no | off | 0 | 0.017911 | 0.14727
SmallOffice | 4 | no | on | 0.023753 | 0.0078055 | 0.11586
SmallOffice | 4 | no | off | 0 | 0.01817 | 0.1187
SmallOffice | 5 | no | on | 0.043092 | 0.007448 | 0.10956
SmallOffice | 5 | no | off | 0 | 0.01636 | 0.11729
SmallOffice | 6 | no | on | 0.020797 | 0.0068475 | 0.076386
SmallOffice | 6 | no | off | 0 | 0.015431 | 0.078379
SmallOffice | 7 | no | on | 0.048833 | 0.0075635 | 0.092015
SmallOffice | 7 | no | off | 0 | 0.015208 | 0.094703
SmallOffice | 8 | no | on | -0.029808 | 0.010959 | 0.13108
SmallOffice | 8 | no | off | 0 | 0.016608 | 0.10461
RetailStandalone | 1 | no | on | -0.022595 | -0.004433 | 0.042866
RetailStandalone | 1 | no | off | 0 | 0.0086578 | 0.057732
RetailStandalone | 2 | no | on | -0.0047537 | -0.0014044 | 0.030713
RetailStandalone | 2 | no | off | 0 | 0.0096851 | 0.052372
RetailStandalone | 3 | no | on | -0.062893 | 0.0072249 | 0.044744
RetailStandalone | 3 | no | off | 0 | 0.011087 | 0.059317
RetailStandalone | 4 | no | on | -0.058131 | 0.0072576 | 0.043559
RetailStandalone | 4 | no | off | 0 | 0.011233 | 0.052274
RetailStandalone | 5 | no | on | -0.044075 | 0.0066422 | 0.037599
RetailStandalone | 5 | no | off | 0 | 0.010005 | 0.049293
RetailStandalone | 6 | no | on | -0.045314 | 0.0053644 | 0.031663
RetailStandalone | 6 | no | off | 0 | 0.0086109 | 0.040649
RetailStandalone | 7 | no | on | -0.045003 | 0.0062664 | 0.03738
RetailStandalone | 7 | no | off | 0 | 0.0093164 | 0.04564
RetailStandalone | 8 | no | on | -0.059189 | 0.0068637 | 0.046638
RetailStandalone | 8 | no | off | 0 | 0.0087033 | 0.067678
RetailStripmall | 1 | no | on | 0.030616 | -0.0020934 | 0.034034
RetailStripmall | 1 | no | off | 0 | 0.012743 | 0.044764
RetailStripmall | 2 | no | on | 0.022752 | -0.0016212 | 0.029919
RetailStripmall | 2 | no | off | 0 | 0.01003 | 0.044994
RetailStripmall | 3 | no | on | 0.0036785 | 0.0049897 | 0.046039
RetailStripmall | 3 | no | off | 0 | 0.0097354 | 0.059559
RetailStripmall | 4 | no | on | 0.0051137 | 0.005938 | 0.036782
RetailStripmall | 4 | no | off | 0 | 0.0099781 | 0.044135
RetailStripmall | 5 | no | on | 0.01644 | 0.0054082 | 0.035997
RetailStripmall | 5 | no | off | 0 | 0.0090268 | 0.047119
RetailStripmall | 6 | no | on | 0.0016928 | 0.0048064 | 0.022476
RetailStripmall | 6 | no | off | 0 | 0.0081319 | 0.028007
RetailStripmall | 7 | no | on | 0.007034 | 0.0057216 | 0.02924
RetailStripmall | 7 | no | off | 0 | 0.0087038 | 0.036165
RetailStripmall | 8 | no | on | -0.018662 | 0.0063118 | 0.04458
RetailStripmall | 8 | no | off | 0 | 0.0082682 | 0.059119
HighriseApartment | 1 | yes | on | 0.10092 | 0.02315 | 0.024259
HighriseApartment | 1 | yes | off
HighriseApartment | 2 | yes | on | 0.1237 | 0.026401 | 0.011922
HighriseApartment | 2 | yes | off
HighriseApartment | 3 | yes | on | 0.12822 | 0.029998 | 0.026898
HighriseApartment | 3 | yes | off
HighriseApartment | 4 | yes | on | 0.15654 | 0.029226 | 0.022081
HighriseApartment | 4 | yes | off
HighriseApartment | 5 | yes | on | 0.19152 | 0.026444 | 0.020718
HighriseApartment | 5 | yes | off
HighriseApartment | 6 | yes | on | 0.1689 | 0.023158 | 0.014267
HighriseApartment | 6 | yes | off
HighriseApartment | 7 | yes | on | 0.22296 | 0.024004 | 0.017173
HighriseApartment | 7 | yes | off
HighriseApartment | 8 | yes | on | 0.22016 | 0.024673 | 0.023371
HighriseApartment | 8 | yes | off
Hospital | 1 | yes | on | 0.14356 | -0.00013311 | 0.0050186
Hospital | 1 | yes | off
Hospital | 2 | yes | on | 0.14669 | -0.00012932 | 0.0031695
Hospital | 2 | yes | off
Hospital | 3 | yes | on | 0.14024 | 0.00062739 | 0.0047621
Hospital | 3 | yes | off
Hospital | 4 | yes | on | 0.14193 | 0.00054771 | 0.0040655
Hospital | 4 | yes | off
Hospital | 5 | yes | on | 0.13975 | 0.00066422 | 0.0045216
Hospital | 5 | yes | off
Hospital | 6 | yes | on | 0.14191 | 0.00056708 | 0.0023928
Hospital | 6 | yes | off
Hospital | 7 | yes | on | 0.13677 | 0.00080465 | 0.004453
Hospital | 7 | yes | off
Hospital | 8 | yes | on | 0.13642 | 0.0011959 | 0.0040444
Hospital | 8 | yes | off
LargeHotel | 1 | yes | on | 0.47471 | 0.032096 | 0.034197
LargeHotel | 1 | yes | off
LargeHotel | 2 | yes | on | 0.49962 | 0.023313 | 0.030274
LargeHotel | 2 | yes | off
LargeHotel | 3 | yes | on | 0.60506 | 0.0048521 | 0.03845
LargeHotel | 3 | yes | off
LargeHotel | 4 | yes | on | 0.60807 | 0.0053411 | 0.031519
LargeHotel | 4 | yes | off
LargeHotel | 5 | yes | on | 0.59262 | 0.0075516 | 0.030408
LargeHotel | 5 | yes | off
LargeHotel | 6 | yes | on | 0.61053 | 0.0046377 | 0.02155
LargeHotel | 6 | yes | off
LargeHotel | 7 | yes | on | 0.57598 | 0.009495 | 0.023619
LargeHotel | 7 | yes | off
LargeHotel | 8 | yes | on | 0.51854 | 0.014087 | 0.034196
LargeHotel | 8 | yes | off
MediumOffice | 1 | yes | on | -0.024874 | -0.0014025 | 0.016071
MediumOffice | 1 | yes | off | 0 | 0.012901 | 0.038318
MediumOffice | 2 | yes | on | -0.0092047 | -0.00054343 | 0.011559
MediumOffice | 2 | yes | off | 0 | 0.016907 | 0.031441
MediumOffice | 3 | yes | on | -0.040296 | 0.0016391 | 0.019011
MediumOffice | 3 | yes | off | 0 | 0.017628 | 0.040227
MediumOffice | 4 | yes | on | -0.045345 | 0.0017748 | 0.019682
MediumOffice | 4 | yes | off | 0 | 0.017674 | 0.034237
MediumOffice | 5 | yes | on | -0.063403 | 0.002367 | 0.021915
MediumOffice | 5 | yes | off | 0 | 0.015646 | 0.034663
MediumOffice | 6 | yes | on | -0.032803 | 0.0011403 | 0.014474
MediumOffice | 6 | yes | off | 0 | 0.014143 | 0.026525
MediumOffice | 7 | yes | on | -0.067527 | 0.0024988 | 0.020783
MediumOffice | 7 | yes | off | 0 | 0.014347 | 0.030073
MediumOffice | 8 | yes | on | -0.056857 | 0.003261 | 0.016715
MediumOffice | 8 | yes | off | 0 | 0.014423 | 0.035897
MidriseApartment | 1 | yes | on | 0.06599 | 0.0072986 | 0.040246
MidriseApartment | 1 | yes | off
MidriseApartment | 2 | yes | on | 0.070883 | 0.0088226 | 0.026537
MidriseApartment | 2 | yes | off
MidriseApartment | 3 | yes | on | 0.074819 | 0.01169 | 0.043576
MidriseApartment | 3 | yes | off
MidriseApartment | 4 | yes | on | 0.086478 | 0.011965 | 0.035587
MidriseApartment | 4 | yes | off
MidriseApartment | 5 | yes | on | 0.11161 | 0.010574 | 0.033958
MidriseApartment | 5 | yes | off
MidriseApartment | 6 | yes | on | 0.087671 | 0.0097381 | 0.023303
MidriseApartment | 6 | yes | off
MidriseApartment | 7 | yes | on | 0.1141 | 0.010318 | 0.028243
MidriseApartment | 7 | yes | off
MidriseApartment | 8 | yes | on | 0.09384 | 0.011065 | 0.038787
MidriseApartment | 8 | yes | off
PrimarySchool | 1 | yes | on | -0.0028214 | -0.00073239 | 0.027825
PrimarySchool | 1 | yes | off | 0 | 0.0040635 | 0.042585
PrimarySchool | 2 | yes | on | -0.003145 | -0.00048868 | 0.025243
PrimarySchool | 2 | yes | off | 0 | 0.0051613 | 0.034707
PrimarySchool | 3 | yes | on | -0.014001 | 0.0021945 | 0.037162
PrimarySchool | 3 | yes | off | 0 | 0.006966 | 0.051381
PrimarySchool | 4 | yes | on | -0.014625 | 0.0027358 | 0.032595
PrimarySchool | 4 | yes | off | 0 | 0.0073028 | 0.039575
PrimarySchool | 5 | yes | on | -0.013364 | 0.0026972 | 0.033315
PrimarySchool | 5 | yes | off | 0 | 0.0065341 | 0.042119
PrimarySchool | 6 | yes | on | -0.013412 | 0.0021701 | 0.020052
PrimarySchool | 6 | yes | off | 0 | 0.0055693 | 0.030458
PrimarySchool | 7 | yes | on | -0.01438 | 0.0029537 | 0.026733
PrimarySchool | 7 | yes | off | 0 | 0.0060382 | 0.035953
PrimarySchool | 8 | yes | on | -0.031734 | 0.0035193 | 0.036547
PrimarySchool | 8 | yes | off | 0 | 0.0056584 | 0.050122
SecondarySchool | 1 | yes | on | 0.1024 | 0.00023945 | 0.086968
SecondarySchool | 1 | yes | off | 0 | 0.012486 | 0.11307
SecondarySchool | 2 | yes | on | 0.068862 | -0.0025184 | 0.088765
SecondarySchool | 2 | yes | off | 0 | 0.012829 | 0.099766
SecondarySchool | 3 | yes | on | 0.065908 | 0.0086722 | 0.11064
SecondarySchool | 3 | yes | off | 0 | 0.017833 | 0.13735
SecondarySchool | 4 | yes | on | 0.073188 | 0.010161 | 0.093551
SecondarySchool | 4 | yes | off | 0 | 0.018479 | 0.10625
SecondarySchool | 5 | yes | on | 0.10456 | 0.0086771 | 0.091988
SecondarySchool | 5 | yes | off | 0 | 0.016491 | 0.11004
SecondarySchool | 6 | yes | on | 0.082164 | 0.0068405 | 0.061696
SecondarySchool | 6 | yes | off | 0 | 0.013164 | 0.081636
SecondarySchool | 7 | yes | on | 0.10561 | 0.0092622 | 0.076459
SecondarySchool | 7 | yes | off | 0 | 0.015229 | 0.09552
SecondarySchool | 8 | yes | on | 0.03254 | 0.0095056 | 0.11767
SecondarySchool | 8 | yes | off | 0 | 0.013243 | 0.13379
SmallHotel | 1 | yes | on | 0.052705 | 0.0034995 | 0.0067916
SmallHotel | 1 | yes | off
SmallHotel | 2 | yes | on | 0.046676 | 0.0056804 | 0.0048768
SmallHotel | 2 | yes | off
SmallHotel | 3 | yes | on | 0.031194 | 0.006518 | 0.0089499
SmallHotel | 3 | yes | off
SmallHotel | 4 | yes | on | 0.029606 | 0.0068726 | 0.0081702
SmallHotel | 4 | yes | off
SmallHotel | 5 | yes | on | 0.033591 | 0.0066767 | 0.0075994
SmallHotel | 5 | yes | off
SmallHotel | 6 | yes | on | 0.027076 | 0.0056615 | 0.0059885
SmallHotel | 6 | yes | off
SmallHotel | 7 | yes | on | 0.027262 | 0.0067599 | 0.0068236
SmallHotel | 7 | yes | off
SmallHotel | 8 | yes | on | 0.012833 | 0.0076459 | 0.0087861
SmallHotel | 8 | yes | off
SmallOffice | 1 | yes | on | 0.046434 | -0.0018424 | 0.11258
SmallOffice | 1 | yes | off | 0 | 0.01927 | 0.13321
SmallOffice | 2 | yes | on | 0.029124 | -0.0023813 | 0.10826
SmallOffice | 2 | yes | off | 0 | 0.019532 | 0.11869
SmallOffice | 3 | yes | on | 0.016941 | 0.0067141 | 0.12801
SmallOffice | 3 | yes | off | 0 | 0.018559 | 0.14456
SmallOffice | 4 | yes | on | 0.019619 | 0.0081361 | 0.11408
SmallOffice | 4 | yes | off | 0 | 0.018817 | 0.11596
SmallOffice | 5 | yes | on | 0.039077 | 0.007786 | 0.10779
SmallOffice | 5 | yes | off | 0 | 0.016967 | 0.11449
SmallOffice | 6 | yes | on | 0.016183 | 0.0071768 | 0.07517
SmallOffice | 6 | yes | off | 0 | 0.016087 | 0.075481
SmallOffice | 7 | yes | on | 0.044565 | 0.0079227 | 0.09018
SmallOffice | 7 | yes | off | 0 | 0.015784 | 0.09127
SmallOffice | 8 | yes | on | -0.035764 | 0.011454 | 0.12951
SmallOffice | 8 | yes | off | 0 | 0.017368 | 0.10014
RetailStandalone | 1 | yes | on | -0.081524 | -0.0037807 | 0.04553
RetailStandalone | 1 | yes | off | 0 | 0.012536 | 0.081666
RetailStandalone | 2 | yes | on | -0.055038 | -0.0016532 | 0.036399
RetailStandalone | 2 | yes | off | 0 | 0.013876 | 0.074217
RetailStandalone | 3 | yes | on | -0.14105 | 0.0089081 | 0.052708
RetailStandalone | 3 | yes | off | 0 | 0.015728 | 0.084177
RetailStandalone | 4 | yes | on | -0.14115 | 0.0086049 | 0.052674
RetailStandalone | 4 | yes | off | 0 | 0.015917 | 0.074226
RetailStandalone | 5 | yes | on | -0.13601 | 0.0082176 | 0.048129
RetailStandalone | 5 | yes | off | 0 | 0.014172 | 0.069976
RetailStandalone | 6 | yes | on | -0.12215 | 0.0064278 | 0.037316
RetailStandalone | 6 | yes | off | 0 | 0.012213 | 0.057649
RetailStandalone | 7 | yes | on | -0.14129 | 0.0079261 | 0.047455
RetailStandalone | 7 | yes | off | 0 | 0.013199 | 0.064803
RetailStandalone | 8 | yes | on | -0.15692 | 0.0087737 | 0.056708
RetailStandalone | 8 | yes | off | 0 | 0.012339 | 0.09598
RetailStripmall | 1 | yes | on | 0.039469 | -0.0026267 | 0.0338
RetailStripmall | 1 | yes | off | 0 | 0.015433 | 0.047342
RetailStripmall | 2 | yes | on | 0.041293 | -0.0027276 | 0.02795
RetailStripmall | 2 | yes | off | 0 | 0.011761 | 0.050781
RetailStripmall | 3 | yes | on | 0.0042823 | 0.00589 | 0.047739
RetailStripmall | 3 | yes | off | 0 | 0.011215 | 0.066054
RetailStripmall | 4 | yes | on | 0.0028853 | 0.006934 | 0.038718
RetailStripmall | 4 | yes | off | 0 | 0.011431 | 0.048617
RetailStripmall | 5 | yes | on | 0.012848 | 0.006467 | 0.038236
RetailStripmall | 5 | yes | off | 0 | 0.010334 | 0.052341
RetailStripmall | 6 | yes | on | -0.0017935 | 0.0055184 | 0.023779
RetailStripmall | 6 | yes | off | 0 | 0.0092673 | 0.031192
RetailStripmall | 7 | yes | on | 0.0001995 | 0.0068505 | 0.031356
RetailStripmall | 7 | yes | off | 0 | 0.009967 | 0.040234
RetailStripmall | 8 | yes | on | -0.026236 | 0.0072638 | 0.048615
RetailStripmall | 8 | yes | off | 0 | 0.009433 | 0.066704