# ComStock Change

Enable Demand Control Ventilation in California (DEER) Models

Implementer: Amy LeBar

Change Document Author: Amy LeBar

Reviewer: Matthew Dahlhausen

# Description of Change

## Summary

This updates ComStock to enable demand control ventilation (DCV) in California models based on California Title 24 code requirements.

# Demand Control Ventilation

## DCV in ComStock

DCV is included in ComStock models when required by the governing ASHRAE 90.1 energy code for the specific spaces/systems in the model. ComStock gathers the necessary criteria for determining DCV requirements and includes DCV functionality only if the space/system requires. Requirement criteria for DCV includes space floor area, space design occupant density, system economizer prevalence, system design outdoor air flow rate, and system energy recovery prevalence. The 90.1 code year for a model is based on the year of the model’s last major HVAC replacement.

## California Implementation Method

Currently, California ComStock models do not have DCV implemented. This update will enable DCV in models that require it according to California Title 24 energy codes (Table 1). Title 24 code versions are not available online prior to the 2007 code year, which makes it difficult to determine whether DCV was required in prior code years. ASHRAE 90.1-2004 has DCV provisions, and because Title 24 follows similar requirements to 90.1, ComStock DEER 2003 models will have DCV enabled in accordance with Title 24-2007 requirements. ComStock DEER 1996, 1985 and Pre-1975 models will not have DCV enabled; the Title 24 versions from the corresponding code years are not available, and ASHRAE 90.1 versions for similar years do not have DCV provisions.

Table 1. California Title 24 DCV Code Requirements by Code Year

| California Title 24 Code Year | DEER Prototype Model(s) | DCV Code Requirements | Exceptions |
| --- | --- | --- | --- |
| Pre-1975 | ComStock DEER Pre-1975 | -- | -- |
| 1985 | ComStock DEER 1985 | -- | -- |
| 1996 | ComStock DEER 1996 | -- | -- |
| 2004 | ComStock DEER 2003 | HVAC single-zone systems with the following characteristics: - Have an air economizer Serve a space with design occupancy ≤40sqftperson ** Follows California Title 24-2007 | - Classrooms are not required to have demand control ventilation. - Where space exhaust is greater than the design ventilation rate specified in 121 (b) 2 B minus 0.2 cfm per ft2 of conditioned area. Spaces that have processes or operations that generate dusts, fumes, mists, vapors or gases and are not provided with local exhaust ventilation (such as indoor operation of internal combustion engines or areas designated for unvented food service preparation). |
| 2007 | ComStock DEER 2007 | HVAC single-zone systems with the following characteristics: - Have an air economizer - Serve a space with design occupancy ≤40sqftperson | - Classrooms are not required to have demand control ventilation. - Where space exhaust is greater than the design ventilation rate specified in 121 (b) 2 B minus 0.2 cfm per ft2 of conditioned area. - Spaces that have processes or operations that generate dusts, fumes, mists, vapors or gases and are not provided with local exhaust ventilation (such as indoor operation of internal combustion engines or areas designated for unvented food service preparation). |
| 2010 | ComStock DEER 2011 | HVAC systems with the following characteristics: - Have an air economizer - Serve a space with design occupancy ≤40sqftperson - Are either - Single zone systems with any controls - Multiple zone systems with Direct Digital Controls (DDC) to the zone level | - Classrooms, call centers, office spaces served by multiple zone systems that are continuously occupied during normal business hours with occupant density greater than 25 people per 1000 ft2, health care facilities and medical buildings, and public areas of social services buildings are not required to have demand control ventilation. - Where space exhaust is greater than the design ventilation rate specified in Section 121(b)2B minus 0.2 cfm per ft2 of conditioned area. - Spaces that have processes or operations that generate dusts, fumes, mists, vapors or gases and are not provided with local exhaust ventilation, such as indoor operation of internal combustion engines or areas designated for unvented food service preparation, or beauty salons shall not install demand control ventilation. - Spaces with an area of less than 150 square feet, or a design occupancy of less than 10 people per Section 121(b)2B. |
| 2013 | ComStock DEER 2014, ComStock DEER 2015 | Spaces with all of the following: - Served by single zone units with any controls or multiple zone systems with DDC to the zone level - Design occupancy ≤40sqftperson - Has an air economizer | - The following spaces are permitted to use DCV but are not required to: classrooms, call centers, office spaces served by multiple zone systems that are continuously occupied during normal business hours with occupant density greater than 25 people per 1000 ft² per §120.1(b)2B, healthcare facilities and medical buildings, and public areas of social services buildings. - Where the space exhaust is greater than the required ventilation rate minus 0.2 cfm/ft². - DCV devices are not allowed in the following spaces: Spaces that have processes or operations that generate dusts, fumes, mists, vapors, or gases and are not provided with local exhaust ventilation, such as indoor operation of internal combustion engines or areas designated for unvented food service preparation, or beauty salons. - Spaces with an area of less than 150 ft², or a design occupancy of less than 10 people per §120.1(b)2B. - Spaces less than 1500 ft² that comply with §120.1(c)5 Occupant Sensor Ventilation Control Devices. |
| 2016 | ComStock DEER 2017 | Spaces with all of the following: - Served by single zone units with any controls or multiple zone systems with Direct Digital Controls to the zone level - Design occupancy ≤40sqftperson - Has an air economizer | - The following spaces are permitted to use DCV but are not required to: classrooms, call centers, office spaces served by multiple zone systems that are continuously occupied during normal business hours with occupant density greater than 25 people per 1000 ft² per §120.1(b)2B, healthcare facilities and medical buildings, and public areas of social services buildings. - Where the space exhaust is greater than the required ventilation rate minus 0.2 cfm/ft². - DCV devices are not allowed in the following spaces: Spaces that have processes or operations that generate dusts, fumes, mists, vapors, or gases and are not provided with local exhaust ventilation, such as indoor operation of internal combustion engines or areas designated for unvented food service preparation, or beauty salons. - Spaces with an area of less than 150 ft², or a design occupancy of less than 10 people per §120.1(b)2B. - Spaces less than 1500 ft² that comply with §120.1(c)5 - Occupant Sensor Ventilation Control Devices. |
| 2019 | ComStock DEER 2020 | Design occupancy ≤40sqftperson AND has at least one of: - An air economizer - Modulating outside air control - Design outdoor airflow rate >3,000 cfm | - The space exhaust is greater than the required ventilation rate minus 0.2 cfm/ft². - DCV devices are not allowed in spaces that have processes or operations that generate dusts, fumes, mists, vapors, or gases and are not provided with local exhaust ventilation, such as indoor operation of internal combustion engines, areas designated for unvented food service preparation, daycare, sickroom, science lab, barber shop, or beauty and nail salons. - Spaces with an area of less than 150 sq. ft., or a design occupancy of less than 10 people, per §120.1(c)3. |

# Software Changes

From a software perspective, this change only requires modifications to OpenStudio-Standards. Changes were made in two areas: (1) ventilation requirements in the OpenStudio-Standards spreadsheets, and (2) thermal zone and air loop code requirements in standards Ruby scripts.

## Ventilation Requirements

Previous DEER ventilation requirements in OpenStudio-Standards were determined implicitly from the DEER models, and most all space types only had per-area ventilation values. As DCV is dependent on  occupancy to modulate ventilation rates, per-person and new per-area values were pulled from Title 24 minimum ventilation rates. Table 2 provides the minimum ventilation rates for Title 24 “Types of Use” and their corresponding DEER space types. Title 24 per-person ventilation requirements were 15 CFM/person. These values are the same for Title 24 years 2007 – 2019.

Table 2. California Title 24 Minimum Ventilation Rates with Corresponding DEER Space Types

| California Title 24 Type of Use | DEER Space Type | CFMft2 conditioned floor area | Notes |
| --- | --- | --- | --- |
| Auto repair workshops | Shop | 1.50 | “Shop” space type is educational shop (e.g., wood shop, autobody shop, etc.) |
| Barber shops | -- | 0.40 |  |
| Bars, cocktail lounges, and casinos | BarCasino | 0.20 |  |
| Beauty shops | -- | 0.40 |  |
| Coin-operated dry cleaning | -- | 0.30 | “Laundry” space types present in hotels and motels, and are assumed to be commercial laundry spaces (i.e., for cleaning staff to wash sheets and towels) and not for guest use |
| Commercial dry-cleaning | Laundry | 0.45 |  |
| High-rise residential | -- | Ventilation Rates Specified by the CBC and CMC |  |
| Hotel guest rooms (less than 500 ft2) | -- | 30 cfm/guest room |  |
| Hotel guest rooms (500 ft2 or greater) | GuestRmOcc, GuestRmUnOcc | 0.15 |  |
| Retail stores | RetailSales, GrocSales | 0.20 |  |
| All others | All others | 0.15 |  |

## Thermal Zone and Air Loop Requirements in Ruby Scripts

Several changes to the OpenStudio-Standards Ruby scripts were required to add DCV to the DEER model workflow. DCV code provisions include specifications for minimum outdoor air (OA) flowrate and/or design occupancy, which are defined in OpenStudio-Standards in the AirLoopHVAC.rb and ThermalZone.rb scripts, respectively. Table 3 provides a summary of these changes to each DEER model year.

Table 3. Changes to OpenStudio-Standards Ruby Scripts

| DEER Prototype Model | AirLoopHVAC.rb Changes |  | ThermalZone.rb Changes |  |
| --- | --- | --- | --- | --- |
|  | Create or Modify | Values | Create or Modify | Values |
| ComStock DEER Pre-1975 | -- | -- | -- | -- |
| ComStock DEER 1985 | -- | -- | -- | -- |
| ComStock DEER 1996 | -- | -- | -- | -- |
| ComStock DEER 2003 | -- | -- | Create | Design occupancy ≤40sqftperson |
| ComStock DEER 2007 | -- | -- | Create | Design occupancy ≤40sqftperson |
| ComStock DEER 2011 | -- | -- | Create | Design occupancy ≤40sqftperson |
| ComStock DEER 2014 | -- | -- | Create | Design occupancy ≤40sqftperson |
| ComStock DEER 2015 | -- | -- | Create | Design occupancy ≤40sqftperson |
| ComStock DEER 2017 | -- | -- | Create | Design occupancy ≤40sqftperson |
| ComStock DEER 2020 | Modify | Min. OA w/o economizer = 3,000 CFM Min. OA w/ economizer = 0 CFM | Create | Design occupancy ≤40sqftperson |

** OA: Outdoor Air

# Impact of Change

TBD

## National Scale Impact

TBD

## Distribution of Total Energy Consumption Impacts

TBD

# Changes in Aggregate Statistics

## Changes Associated with Upgrades

TBD

## Changes in Baseline Model Characteristics

TBD

# Changes in Upgrade Savings Estimates

TBD